## POTW Monitoring Data Summary
POTW Monitoring Data Summary
Pollutant | Local Limits | [5 empty] | Influent |  |  |  |  | Effluent |  |  |  |  | Biosolids
| Units | Daily Max | Monthly Average | MAIL (lb/day) | Other (specify) | Other (Specify) | Units | Quantification Level | Maximum Monthly Average | Maximum | # samples | Units | Maximum Monthly Average | Daily Max | Quantification Level | # samples | Units | Maximum Monthly Average | Daily Max | Quantification Level | # samples
Arsenic | ug/L | 26 |  | 0.15245 |  |  | ug/L |  |  |  |  | mg/L |  |  |  |  | mg/kg | 61.4 | 61.4 | 61.1 | 2
Cadmium | ug/L | 2 |  | 0.011727 |  |  | ug/L | <0.5 | 1.65 | 1.9 | 24 | ug/L | 1.7 | 1.7 | <0.5 | 24 | mg/kg | <6.1 | <6.1 | 6.1 | 2
Chromium | ug/L | 369 |  | 2.1637 |  |  | ug/L |  | 9.75 | 14.1 | 24 | ug/L | <3.0 | <3.0 | <3.0 | 24 | mg/kg | 119 | 119 | 30.6 | 2
Copper | ug/L | 99 |  | 0.58049 |  |  | ug/L | <50 | 165 | 220 | 48 | ug/L | <50 | <50 | 50 | 48 | mg/kg | 897 | 897 | 6.1 | 2
Cyanide | ug/L | 4 |  | 0.023454 | [7 empty] | ug/L | <2 | <2 | <2 | 12
Lead | ug/L | 100 |  | 0.58636 |  |  | ug/L | <2.0 | 118.2 | 50 | 64 | ug/L | 9.28 | 12 | <2.0 | 64 | mg/kg | 32 | 32 | 30.6 | 2
Mecury | ug/L | Report |  |  |  |  | ug/L | 0.2 | <0.2 | <0.2 | 4 | ng/L | 0.606 | 0.606 | 0.5 | 4 | mg/kg | <1.2 | <1.2 | 1.2 | 2
Molybdenum | ug/L | 118 |  | 0.6919 |  |  | ug/L | 10 | 27.66 | 41 | 64 | ug/L | 22 | <50 | <10 | 64 | mg/kg | <61.1 | <61.1 | 61.1 | 2
Nickel | ug/L | 185 |  | 1.0848 |  |  | ug/L | <50 | 61 | 65 | 24 | ug/L | 66.5 | 68 | <50 | 24 | mg/kg | 31.1 | 31.1 | 6.1 | 2
Silver | ug/L | 3 |  | 0.017591 |  |  | ug/L | <2.0 | 4.47 | 8.7 | 48 | ug/L | <2.0 | <2.0 | <2.0 | 48 | mg/kg | <6.1 | <6.1 | 6.1 | 2
Zinc | ug/L | 835 |  | 4.8961 |  |  | ug/L | <50 | 261.67 | 440 | 64 | ug/L | 59 | 92 | <50 | 64 | mg/kg | 1170 | 1170 | 30.6 | 2
Ammonia | ug/L | Report |  |  |  |  | mg/L | <0.3 | 34.4 | 59 | 261 | mg/L | 0.475 | 2.11 | <0.3 | 261 | mg/kg | 84600 | 84600 | 1540 | 2
BOD 5-day | ug/L | Report |  |  |  |  | mg/L | 2 | 290.79 | >375 | 261 | mg/L | 9.2 | >23.7 | 2 | 261
Solids, Total | ug/L | Report |  |  |  |  | mg/L |  | 321.73 | 1568 | 261 | mg/L | 7.15 | 12.5 |  | 261 | % | 3.02 | 3.72 |  | 13
BTEX MDNR Scan 2 | ug/L | 100 |  | 0.58636 | [12 empty] | ug/kg | 20 | 20 | 20 | 1