## POTW Monitoring Data Summary
POTW Monitoring Data Summary
Pollutant | Local Limits | [5 empty] | Influent |  |  |  |  | Effluent |  |  |  |  | Biosolids
| Units | Daily Max | Monthly Average | MAIL (lb/day) | Other (specify) | Other (Specify) | Units | Quantification Level | Maximum Monthly Average | Maximum | # samples | Units | Maximum Monthly Average | Daily Max | Quantification Level | # samples | Units | Maximum Monthly Average | Daily Max | Quantification Level | # samples
Arsenic | ug/L | 26 |  | 0.15245 |  |  | ug/L |  |  |  |  | mg/L | <0.001 | <0.001 |  | 1 | mg/kg | 26.6 | 26.6 | 3 | 2
Cadmium | ug/L | 2 |  | 0.011727 |  |  | ug/L | <0.5 | 2.51 | 2.72 | 24 | ug/L | 2.55 | 2.58 | <0.5 | 24 | mg/kg | <3.8 | <3.8 | 3.8 | 2
Chromium | ug/L | 369 |  | 2.1637 |  |  | ug/L |  | 10 | 10.2 | 24 | ug/L | 2.86 | <3.0 |  | 24 | mg/kg | 97.2 | 97.2 | 3 | 2
Copper | ug/L | 99 |  | 0.58049 |  |  | ug/L | <50 | 121.5 | 162 | 48 | ug/L | <50 | <50 | <50 | 48 | mg/kg | 1020 | 1020 | 31 | 2
Cyanide | ug/L | 4 |  | 0.023454 | [7 empty] | ug/L | <2 | <2 | 2 | 12
Lead | ug/L | 100 |  | 0.58636 |  |  | ug/L | <2.0 | 11.28 | 14.8 | 64 | ug/L | 8.2 | 10.7 | <2.0 | 64 | mg/kg | <38 | <38 | 25 | 2
Mecury | ug/L | Report |  |  |  |  | ug/L |  | 0.2 | 0.2 |  | ng/L | 1.76 | 1.76 | 0.5 |  | mg/kg | 0.57 | 0.57 | 0.22 | 2
Molybdenum | ug/L | 118 |  | 0.6919 |  |  | ug/L |  | 16.33 | 27 | 64 | ug/L | 16.05 | 22.9 |  | 64 | mg/kg | 25 | 25 | 9.9 | 2
Nickel | ug/L | 185 |  | 1.0848 |  |  | ug/L | <50 | 54.5 | 59 | 24 | ug/L | 53 | 56 | <50 | 24 | mg/kg | 24.3 | 24.3 | 9.9 | 2
Silver | ug/L | 3 |  | 0.017591 |  |  | ug/L | <2.0 | 2.26 | 3.25 | 48 | ug/L | 2.45 | 3.88 | <2.0 | 48 | mg/kg | 4 | 4 | 2
Zinc | ug/L | 835 |  | 4.8961 |  |  | ug/L | <50 | 218 | 300 | 64 | ug/L | 53 | 76 | <50 | 64 | mg/kg | 1480 | 1480 | 20 | 2
Ammonia | ug/L | Report |  |  |  |  | mg/L |  | 30.47 | 42.8 | 221 | mg/L | 0.68 | 4.62 |  | 221 | mg/kg | 39900 | 39900 | 1300 | 2
BOD 5-day | ug/L | Report
Solids, Total | ug/L | Report | [14 empty] | % | 8.02 | 8.24 | 0.01 | 16
BTEX MDNR Scan 2 | ug/L | 100 |  | 0.58636 | [7 empty] | ug/L | <5 | <5 | 5 | 1 | ug/kg | <6000 | <6000 | 6000 | 1